[Site]

RCD Testing Logbook

[Year]

Contents

Section 1		Introduction

Section 2		Procedure(s)

Section 3		Schedule of Tests

Section 4		Skilled and Competent Persons Register

Section 5		Test Equipment Register

Section 6		Test Record Sheets

Section 7		Remedial Actions Record Sheets

Section 8		RCD Location List

Section 9		RCD Location Drawings

Section 10		Guidance Notes

RCD Testing Logbook

There is a requirement of BS7671 to provide Additional Protection by means of Residual Current Devices (RCDs):

411.3.3		Additional Protection

In AC systems, additional protection by means of an RCD with a rated residual operating current not exceeding 30mA shall be provided for:

- Socket-outlets with a rated current not exceeding 32A in locations where they are liable to be used by persons of capability BA1, BA3 or children (BA2, BA3).

- Socket-outlets with a rated current not exceeding 32A in other locations.

- Mobile equipment with a current rating not exceeding 32A for use outdoors.

An exception to (ii) but not (i) or (iii) is permitted where a suitably documented risk assessment is undertaken with the involvement of a skilled person (electrical) determines that RCD protection is not necessary.

BA1 is described as an ordinary person (a person who is neither a skilled nor an instructed person) BA2 as children, and BA3 as disabled.

Amendment 2 of BS7671:2018 (AMD2) introduces a new approach to the testing of RCDs, focusing on verifying that they are capable of operating, rather than verifying that they will provide a particular disconnection time as stated in BS 7671.

To verify the effectiveness of an RCD used to provide automatic disconnection, or to verify the effectiveness of an RCD used to provide additional protection the following inspections and tests are applicable:

- A visual inspection to confirm that the RCD is of an appropriate type and rating for its location and application.

- Testing of the RCD using a suitable test instrument according to BS EN 61557-6.

- Operation of the integral test facility to confirm correct function.

To comply with these requirements the following inspection and tests are recommended:

6 Monthly Tests

These tests involve the operation of the RCD via the integral test device and the results recorded on the Test Record Sheet.

Annual Tests

These tests involve the operation of the RCD via an approved RCD Tester connected to the circuit protected by the RCD. A range of tests are conducted and the results recorded on the Test Record Sheet.

Defects

Any defects that are noted during the testing are to be reported to the Site Manager and recorded on the Defects and Remedial Action Test Sheet.

The Frequency and Scope of the required tests are laid out in the table below:

| Frequency | Scope | Comments |
| --- | --- | --- |
| 6 Monthly | Equipment supplied from the affected circuit should be shutdown and/or disconnected before the test is conducted. Each RCD should be inspected for condition, type and rating. Each RCD should be operated by pressing the integral testing button. The test period should be sufficient only to ensure that the RCD operates All test results are to be recorded in the RCD Testing Log Book All faults are to be recorded in the RCD Testing Log Book and the issue logged on the site CAFM system. | The location of the RCDs is available in the RCD Testing Log Book. The number and location of socket-outlets supplied from the RCD are available in the RCD Testing Log Book. Permission to carry out the tests should be sought manager or supervisor of the area affected. |
| Annually | Affected equipment should be shutdown and/or disconnected before the test is conducted. Each RCD should be inspected for condition, type and rating. Each RCD should be operated by connecting an RCD Tester to the circuit protected by the RCD. The tests to be conducted are: 50% of Rated Current (0.5 In) (RCD should not operate) 100% of Rated Current (In) (RCD should operate in less than 300ms). All test results are to be recorded in the RCD Testing Log Book All faults are to be recorded in the RCD Testing Log Book and the issue logged on the site CAFM system. | The location of the RCDs is available in the RCD Testing Log Book. The number and location of socket-outlets supplied from the RCD are available in the RCD Testing Log Book. Permission to carry out the tests should be sought manager or supervisor of the area affected. |

Schedule of RCD Tests  (Page 1)

| Level | D/Board | Circuit | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |  |
|  |  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |
|  |  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |
|  |  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |
|  |  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |
|  |  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |
|  |  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |
|  |  |  |  |  | A |  |  |  |  |  | 6 |  |  |  |

Test :	6   6 Monthly    A  Annual

| Skilled and Competent Persons Register |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Name | Employed By | Competent Persons |  | Skilled Persons |  | Tasks Authorised (CP) or Completed (SkP) |
|  |  | CP Level | Appointment Date | Authority to Work No | Issue Date |  |

| Test Equipment Register |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment Details |  |  | Inspection “I” and Calibration “C” Record |  |  |  |  |  |
| Make | Model | Serial Number | Date (“I” or “C”) | Date (“I” or “C”) | Date (“I” or “C”) | Date (“I” or “C”) | Date (“I” or “C”) | Date (“I” or “C”) |

RCD Test Record Sheet

| Site: |  |  | Distribution Board: |  |
| --- | --- | --- | --- | --- |
|  |  |  | Location: |  |

| Circuit | Annual Test |  |  |  |  | 6 Monthly Test |  |  | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.5xIΔn ms | 1xIΔnms | ResultRef | Date | Initial | Result Ref | Date | Initial |  |

Test References: 	P  Pass		F   Fail

RCD Defects and Remedial Action Record Sheet

| Site: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date of Test | Distribution Board | Circuit | Description of Fault | Remedial Action |  | Date Repaired | Repairing Technician |  |

RCD Location List

| Level | Location | Distribution Board | Number of RCDs | RCD Protected Circuits | Areas fed from RCD Protected Circuits | No of Outlets Supplied |
| --- | --- | --- | --- | --- | --- | --- |