## Testing
Item No | DB Description | DB Ref | DB Location | DB Ways | Circuits Utilsed |  | Last Test Details | [6 empty] | Remedial Works Complete | Next Test Due | Comments
[5 empty] | SP | TP | Date | Completed By | C1 | C2 | C3 | FI | Result
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
General Inspection Observations
| Today | 2024-04-21 | [5 empty] | Totals | 0 | 0 | 0 | 0 |  | N | Repairs Incomplete
| 6 Month Warning | 2024-10-20 | [5 empty] | Board Count | 22 |  |  |  |  | RA | Issue Risk Assessed
[8 empty] | Circuit Count | 0 |  |  |  |  | Y | Repairs Completed
|  | Main Switchboard | [11 empty] | N/A | No Issus Raised
[8 empty] | Satisfactory | 0 | 0 | %
[8 empty] | Unsatisfactory | 0 | 0 | %
[8 empty] | Remediated | 0 | 0 | %
[10 empty] | 0 | %
[8 empty] | N | 0 | 0 | %
[8 empty] | RA | 0 | 0 | %
[8 empty] | Y | 0 | 0 | %
[8 empty] | N/A | 0 | 0 | %
[10 empty] | 0 | %
Formulas:
DB Ref = SUM([DB Ref, row above]+182)

## Remedials
Oxford Brookes Fixed Wiring Remedial Action Tracker | [6 empty] | Status | Open - No Progress | Item yet to be progressed
[7 empty] | Status | Open - In Progress | Item progressed but not completed
[7 empty] | Status | Closed | Item Completed
[7 empty] | Status | Risk Assessed | Item Risk Assessed and not pursued
Item Number | Test Date | Distribution Board or Switchgear | Circuit Reference | Obsevation |  | Category | Tested By | Status | Comments
1 | 2017-09-16 | MSP 1 |  | MCCB Setings could not be determined |  | FI | PHS | Open - No Progress
2 | 2017-09-16 | DB G1/L | 5L2 | No RCD Protection |  | C3 | PHS | Open - No Progress
3 | 2017-09-16 | DB G1/L |  | No DB Schedule Available |  | C3 | PHS | Open - No Progress
4 | 2017-09-16 | General |  | CPCs Incorrectly Identified |  | C3 | PHS | Open - No Progress
5 | 2017-09-16 | General |  | Line Conductors Incorrectly Identified |  | C3 | PHS | Open - No Progress
6 | 2017-09-16 | MSP 1 | 19TP | Neutral Disconnected and Taped |  | FI | PHS | Open - No Progress
7 | 2017-09-16 | DB G2/P |  | Screws Missing from DB Cover |  | C3 | PHS | Open - No Progress
8 | 2017-09-16 | DB Kitchen |  | Screws Missing from DB Cover |  | C3 | PHS | Open - No Progress
9 | 2017-09-16 | F1/P | 8L3 | Untraced Circuit |  | FI | PHS | Open - No Progress
10 | 2018-10-03 | MSP 1 |  | No Circuit Schedule or Single Line Diagram Available |  | C3 | PHS | Open - No Progress
11 | 2018-10-03 | MSP 1 |  | MCCB Setings could not be determined |  | FI | PHS | Open - No Progress | Repeated from 16/09/17
12 | 2018-10-03 | DB G1/L & P |  | Screws Missing from DB Cover |  | C3 | PHS | Open - No Progress
13 | 2018-10-03 | Boiler Room |  | Main Bonding Conductors to Water and Gas Undersized |  | C3 | PHS | Open - No Progress
14 | 2019-08-27 | DB F2/L |  | Debris left in bottom of DB |  | C3 | PHS | Open - No Progress
15 | 2019-08-27 | DB F2/P |  | Debris left in bottom of DB |  | C3 | PHS | Open - No Progress
16 | 2019-08-27 | DB G2/L |  | No IP2X Protection, Hole in front of DB |  | C3 | PHS | Open - No Progress
17 | 2019-08-27 | DB G2/L | 7/L1 | Cable Damaged |  | C3 | PHS | Open - No Progress
18 | 2020-08-17 | MSP 1 |  | No Alternative Supply Warning Label |  | C3 | PHS | Open - No Progress
19 | 2020-08-18 | DB Kitchen |  | Screws Missing from DB Cover |  | C3 | PHS | Open - No Progress | Repeated from 16/09/17
20 | 2020-08-19 | MSP 1 |  | No Eath Electroode for Mobile Generator |  | FI | PHS | Open - No Progress
21 | 2020-08-20 | MSP 1 |  | Unable to locate Main Protective Bonding Conductor |  | FI | PHS | Open - No Progress
22 | 2020-08-21 | Genersal |  | Wiring in Escape Routes not adequately supported |  | C3 | PHS | Open - No Progress
23
24
25
26
27
28
29
30
[5 empty] | Total | 0 | C1 | Category 1 Non Compliance
[5 empty] | Total | 0 | C2 | Category 2 Non Compliance
[5 empty] | Total | 16 | C3 | Category 3 Non Compliance
[5 empty] | Total | 6 | FI | Further Investigation Required
[5 empty] | Total | 0 | LIM | Test Not Completed due to Limitations on Access or Scope
[5 empty] | Total | 0 | NO | Noted Observation
[5 empty] | Total | 22
[5 empty] | Open - No Progress | 22 | 100 | %
[5 empty] | Open - In Progress | 0 | 0 | %
[5 empty] | Closed | 0 | 0 | %
[5 empty] | Risk Assessed | 0 | 0 | %

## MCP
No | Designation | SP/TP | Rating | Setting | Line mm²
1 | Fire Alarm Supply | SP | 16 |  | 4
2 | DB External | TP | 63 |  | 25
3 | Plant Deck 3 | TP | 63 |  | 16
4
5
6 | DB G1/L, DB G1/P | TP | 160 |  | 35
7 | DB G2/L, DB G2/P | TP | 160 |  | 35
8 | Diabled Refuge Supply | SP | 16 |  | 4
9 | Lift Supply | TP | 32 |  | 10
10 | DB Comms |  | 63 |  | 16
11
12
13 | DB Boiler Room | TP | 160 |  | 70
14 | DB Kitchen | TP | 160 |  | 95
15
16 | Plantdeck 1A | TP | 100 |  | 25
17 | Plantdeck 1B | TP | 63 |  | 16
18 | Plantdeck 2 | TP | 100 |  | 25
19 | AHU 5 Supply | TP | 125 |  | 25
20 | DB F1/L, DB F1/P | TP | 160 |  | 35
21 | DB F2/L, DB F2/P | TP | 160 |  | 35
22
23
24